Sample recording sheets

Monthly temperature checks of the hot and cold water cylinders/tanks

| Date | Outgoing water temperature from the hot water cylinder (should be at least 60 0C) |  |  |  |  |  |  |  |  | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Tank reference number |  |  |  |  |  |  |  |  |  |
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |  |

| Date | Return water temperature to the hot water tanks (if applicable) (should be at least 50 0C) |  |  |  |  |  |  |  |  | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Tank reference number |  |  |  |  |  |  |  |  |  |
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |  |

Monthly temperature checks at the sentinel hot and cold water outlets

| Date | Temperatures at hot water sentinel outlets for each hot water cylinder (refer to schematic) (should reach at least 50 0C within a minute of running the outlet) |  |  |  |  |  |  |  | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Tank 1 |  | Tank 2 |  | Tank 3 |  | Tank 4 |  |  |
|  | nearest | furthest | nearest | furthest | nearest | furthest | nearest | furthest |  |

Notes:  If a thermostatic mixing valve (TMV) is present, use a surface temperature probe for measuring the temperature at the inlet pipe to the TMV

| Date | Temperatures at cold water sentinel outlets for each cold water tank (refer to schematic) (should be less than 20 0C within two minutes of running the outlet) |  |  |  |  |  |  |  | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Tank 1 |  | Tank 2 |  | Tank 3 |  | Tank 4 |  |  |
|  | nearest | furthest | nearest | furthest | nearest | furthest | nearest | furthest |  |

Weekly flushing of infrequently used outlets

(The outlets should be flushed weekly for several minutes)

|  | Outlet number (refer to a plan showing the outlets) |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Date | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 |

Three-monthly cleaning of the shower heads

Dismantle, clean and descale shower heads and hoses or replace

| Date | Shower number (refer to plan) |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 |

Annual temperature testing of a representative number of hot and cold water outlets on a rotational basis

| Water outlet number (on plan) | Date | Temperature at cold water outlet | Temperature at hot water outlet | Comments |
| --- | --- | --- | --- | --- |
| 1 |  |  |  |  |
| 2 |  |  |  |  |
| 3 |  |  |  |  |
| 4 |  |  |  |  |
| 5 |  |  |  |  |
| 6 |  |  |  |  |
| 7 |  |  |  |  |
| 8 |  |  |  |  |
| 9 |  |  |  |  |
| 10 |  |  |  |  |
| 11 |  |  |  |  |
| 12 |  |  |  |  |
| 13 |  |  |  |  |
| 14 |  |  |  |  |
| 15 |  |  |  |  |
| 16 |  |  |  |  |
| 17 |  |  |  |  |
| 18 |  |  |  |  |
| 19 |  |  |  |  |
| 20 |  |  |  |  |
| 21 |  |  |  |  |
| 22 |  |  |  |  |
| 23 |  |  |  |  |
| 24 |  |  |  |  |
| 25 |  |  |  |  |
| 26 |  |  |  |  |
| 27 |  |  |  |  |
| 28 |  |  |  |  |
| 29 |  |  |  |  |
| 30 |  |  |  |  |
| 31 |  |  |  |  |
| 32 |  |  |  |  |
| 33 |  |  |  |  |
| 34 |  |  |  |  |
| 35 |  |  |  |  |